GUIDE SPECIFICATION

Paratech Roof Membrane System

Base in Hot Asphalt/Torch-Applied Cap

Substrate - Lightweight Insulating Concrete or Gypsum With Nailed Base Sheet

Prepared by:

Siplast, Inc.

14911 Quorum Drive

Suite # 600

Dallas, Texas 75254

(800) 922-8800

This specification is provided as a general guide for use of Siplast products based on typical building conditions and standard roofing practices.  Siplast is strictly a manufacturer of roofing systems and has no experience, training or expertise in the areas of architecture/engineering or in the area of consulting with respect to matters related to such areas.  Siplast recommends that the Owner's representative independently verify the accuracy and appropriateness of a specification provided for a specific project.

Siplast recommends that venting provisions be incorporated into lightweight insulating concrete designs.  Contact the roof membrane manufacturer and lightweight insulating concrete supplier for specific information on venting details.

January 1, 2022

SECTION 07 52 16 MODIFIED BITUMINOUS MEMBRANE ROOFING   (Rev 1/1/2022)

PART 1  GENERAL

1.01  SECTION INCLUDES

A.	Substrate Panel Application

B.	Temporary Roof Application

C.	Base Sheet Application

D.	Roof Membrane Application

E.	Roof Flashing Application

1.02  RELATED SECTIONS

A.	Section [-----] - Submittals

B.	Section [-----] - Rough Carpentry

C.	Section [-----] - Roof Decks

D.	Section [-----] - Sheet Metal Flashing Components and Roofing Accessories

E.	Section [-----] - Sheet Metal Flashing and Trim

F.	Section [-----] - Roof Specialties

G.	Section [-----] - Temporary Roofs/Vapor Retarder

*  NOTE:	A vapor retarder can be an important component in roof systems where climatic and building interior conditions require the prevention of vapor condensation within the roof assembly.

1.03  REFERENCE STANDARDS

References in these specifications to standards, test methods, codes etc., are implied to mean the latest edition of each such standard adopted.  The following is an abbreviated list of associations, institutions, and societies which may be used as references throughout this specification section.

ASTM	American Society for Testing and Materials

Philadelphia, PA

FM	Factory Mutual Engineering Research Corp.

Norwood, MA

NRCA	National Roofing Contractors Association

Rosemont, IL

CERTA	Certified Roofing Torch Applicator

Rosemont, IL

OSHA	Occupational Safety and Health Administration

Washington, DC

UL	Underwriters Laboratories

Northbrook, IL

1.04  SUBMITTALS

All submittals which do not conform to the following requirements will be rejected.

*  NOTE:	Coordinate submittal requirements with general provisions.  Modify submittals to suit specific project requirements.

A.	Submittals Prior to Contract Award:

1.	Letter from the proposed primary roofing manufacturer confirming that the bidder is an acceptable Contractor authorized to install the proposed system.

2.	Letter from the primary roofing manufacturer stating that the proposed application will comply with the Manufacturer's requirements in order to qualify the project for the specified guarantee.

1.05  QUALITY ASSURANCE

A.	Acceptable Products:  Provide primary roofing products, including each type of sheet, all manufactured in the United States, supplied by a single manufacturer.  Provide secondary or accessory products which are acceptable to the manufacturer of the primary roofing products.

*  NOTE:	Coordinate the desired fire and windstorm rating with the Underwriters Laboratories Roofing Materials and Systems Directory and the relevant independent wind uplift testing agency.

B.	Agency Approvals:  The proposed roof system shall conform to the following requirements.  No other testing agency approvals will be accepted.

1.	Underwriters Laboratories Class [-----] acceptance of the proposed roofing system.

2.	Evidence by an accredited independent testing agency or agencies that the roof configuration meets a design windload pressure of - [---] psf or greater.

C.	Project Acceptance:  Submit a completed manufacturer's application for roof guarantee form along with shop drawings of the roofs showing all dimensions, penetrations, and details.

D.	Scope of Work:  The work to be performed under this specification shall include but is not limited to the following:  Attend necessary job meetings and furnish competent and full time supervision, experienced roof mechanics, all materials, tools, and equipment necessary to complete, in an acceptable manner, the roof installation in accordance with this specification.  Comply with the latest written application instructions of the manufacturer of the primary roofing products.  In addition, application practice shall comply with requirements and recommendations contained in the latest edition of the Handbook of Accepted Roofing Knowledge (HARK) as published by the National Roofing Contractor's Association, amended to include the acceptance of a phased roof system installation.

E.	Local Regulations:  Conform to regulations of public agencies, including any specific requirements of the city and/or state of jurisdiction.

F.	Manufacturer Requirements:  The primary roofing materials manufacturer shall provide direct trained company personnel to attend necessary job meetings, perform periodic inspections as necessary, and conduct a final inspection upon successful completion of the project.

1.06  PRODUCT DELIVERY STORAGE AND HANDLING

A.	Delivery:  Deliver materials in the manufacturer's original sealed and labeled containers and in quantities required to allow continuity of application.

B.	Storage:  Store materials out of direct exposure to the elements.  Store roll goods on a clean, flat and dry surface.  All material stored on the roof overnight shall be stored on pallets.  Rolls of roofing must be stored on ends.  Store materials on the roof in a manner so as to preclude overloading of deck and building structure.  Store materials such as solvents, adhesives and asphalt cutback products away from open flames, sparks or excessive heat.  Cover all material using a breathable cover such as a canvas.  Polyethylene or other non-breathable plastic coverings are not acceptable.

C.	Handling:  Handle all materials in such a manner as to preclude damage and contamination with moisture or foreign matter.  Handle rolled goods to prevent damage to edges or ends.

D.	Damaged Material:  Any materials that are found to be damaged or stored in any manner other than stated above will be automatically rejected, and will require removal and replacement at the Contractor's expense.

1.07  PROJECT/SITE CONDITIONS

A.	Requirements Prior to Job Start

1.	Notification:  Give a minimum of 5 days notice to the Owner and manufacturer prior to commencing any work and notify both parties on a daily basis of any change in work schedule.

2.	Safety:  Familiarize every member of the application crew with all fire and safety regulations recommended by OSHA, NRCA and other industry or local governmental groups.

B.	Environmental Requirements

1.	Precipitation:  Do not apply roofing materials during precipitation or in the event there is a probability of precipitation during application.  Take adequate precautions to ensure that materials, applied roofing, and building interiors are protected from possible moisture damage or contamination.

2.	Temperature Restrictions - asphalt:  At ambient temperatures of 40F (4C) and below, special precautions must be taken to ensure that the specified Type IV asphalt maintains a minimum acceptable 400F (204C) at the point of sheet application.  Do not overheat asphalt to compensate for cold conditions.  The use of insulated handling equipment is strongly recommended.  Use insulated hot luggers, mop carts, and kettle-to-roof supply lines.  Use hand mops constructed with a smaller yarn head to facilitate short moppings.  Do not fill luggers and mop carts to more than half their capacity at all times.

C.	Protection Requirements

1.	Membrane Protection:  Provide protection against staining and mechanical damage for newly applied roofing and adjacent surfaces throughout this project.

2.	Torch Safety:  Crew members handling torches shall be trained by an Authorized Certified Roofing Torch Applicator (CERTA) Trainer, be certified according to CERTA torch safety guidelines as published by the National Roofing Contractor's Association (NRCA), and follow torch safety practices as required by the contractor's insurance carrier.  Designate one person on each crew to perform a daily fire watch.  The designated crew member shall watch for fires or smoldering materials on all areas during roof construction activity, and for the minimum period required by CERTA guidelines after roofing material application has been suspended for the day.

3.	Debris Removal:  Remove all debris daily from the project site and take to a legal dumping area authorized to receive such materials.

4.	Site Condition:  Complete, to the owner's satisfaction, all job site clean-up including building interior, exterior and landscaping where affected by the construction.

1.08  GUARANTEE

*   NOTE:	The following guarantee entry is applicable when the roof membrane is applied over existing gypsum decks, existing lightweight insulating concrete decks, or where full system coverage of new lightweight insulation concrete is not required.

A.	Roof Membrane Guarantee:  Upon successful completion of the project, and after all post installation procedures have been completed, furnish the Owner with the manufacturer's [10, 15, or 20] year labor and materials membrane guarantee.  The guarantee shall be a term type, without deductibles or limitations on coverage amount, and shall be issued at no additional cost to the Owner.  This guarantee shall not exclude random areas of ponding from coverage.

>	Siplast [10, 15, or 20] year Roof Membrane Guarantee

*   NOTE:	The following guarantee entry is applicable when the roof membrane is applied over a new Siplast lightweight insulating concrete system, allowing for full system coverage to include the new Siplast Lightweight Concrete Insulation System.

A.	Roof System Guarantee:  Upon successful completion of the project, and after all post installation procedures have been completed, furnish the Owner with the roof system manufacturer's [10, 15, or 20] year labor and materials roof system guarantee. The roof system guarantee shall include both the roofing and flashing membranes, and the specified new lightweight insulating concrete system consisting of [aggregate fill], [pre-generated foam], patented-pre-formed polystyrene panels, and base sheet fasteners.  All repair or replacement costs covered under the guarantee shall be borne by the roofing membrane manufacturer.  The guarantee shall be a term type, without deductibles or limitations on coverage amount, and be issued at no additional cost to the Owner.  Specific items covered under the roof system guarantee include:

1.	The actual resistance to heat flow through the roof insulation will be at least 80% of the design thermal resistance, provided that the roofing membrane is free of leaks;

2.	Should a roof leak occur, the insulating performance of the roof insulation will be at least 80% of the design thermal resistance within a 2 year period following repair of the leak.

3.	The roof insulation will remain in a reroofable condition should the roof membrane require replacement (excluding damage caused by fastener pullout during removal of the old membrane.)

4.	The roof insulation material will not cause structural damage to the building as a result of expansion from thermal or chemical action.

>	Siplast [10, 15, or 20] Year Roof System Guarantee

PART 2  PRODUCTS

2.01  ROOFING SYSTEM ASSEMBLY/PRODUCTS

A.	Substrate Panel/Thermal Barrier:  Panels shall be UL and FM approved.  Panels shall be approved in writing by the manufacturer for intended use and for use with the specified roof assembly.

1.	Gypsum Sheathing Panel:  A non-structural gypsum panel composed of fiber reinforced synthetic gypsum.  Provide panels having a nominal thickness of [---] inch.  Acceptable types are as follows:

>	Securock Gypsum-Fiber Roof Board by United States Gypsum; Chicago, IL

2.	Gypsum Sheathing Panel:  A panel composed of a gypsum based, non-structural water resistant core material integrally bonded with fiberglass mats on both sides having a nominal thickness of [---] inch.  The panel surface shall be factory primed with a non-asphaltic primer.  Acceptable types are as follows:

>	DensDeck Prime Gypsum Roof Board, by Georgia Pacific Corporation; Atlanta, GA

3.	Gypsum Sheathing Panel:  A panel composed of a gypsum based, non-structural water resistant core material integrally bonded with fiberglass mats on both sides having a nominal thickness of [---] inch.  The panel surface shall be factory primed with a non-asphaltic primer.  Acceptable types are as follows:

>	DEXcell® FA Glass Mat Roof Board by National Gypsum, Charlotte, NC

B.	Temporary Roof Ply Sheet

1.	Torchable Modified Bitumen Ply Sheet:  A modified bitumen sheet, consisting of a lightweight random fibrous glass mat impregnated and coated with a styrene-butadiene-styrene (SBS) modified bitumen blend having a mineral parting agent surfacing.

>	Siplast Paratech Glass Base TG

2.	Torchable Modified Bitumen Ply Sheet:  A modified bitumen sheet, consisting of a 180-gram polyester mat impregnated and coated with a styrene-butadiene-styrene (SBS) modified bitumen blend having a mineral parting agent surfacing.

>	Siplast Paratech 180 Base TG

3.	Hot Asphalt-applied Modified Bitumen Ply Sheet:  A modified bitumen sheet, consisting of a lightweight random fibrous glass mat impregnated and coated with a styrene-butadiene-styrene (SBS) modified bitumen blend having a mineral parting agent surfacing.

>	Siplast Paratech Glass Base

4.	Hot Asphalt-applied Modified Bitumen Ply Sheet:  A modified bitumen sheet, consisting of a 180-gram polyester mat impregnated and coated with a styrene-butadiene-styrene (SBS) modified bitumen blend having a mineral parting agent surfacing.

>	Siplast Paratech 180 Base

*   NOTE:	Delete the following reference to Specification Section 03 52 00 if existing lightweight insulating concrete or gypsum.

C.	Lightweight Insulating Concrete Roof System:  See Specification Section 03 52 00.

D.	Base Sheet

1.	Base Sheet:  A fiberglass reinforced, asphalt coated sheet with a polyolefin film backing, having a minimum weight of 20 lb/sq.  The sheet shall conform to ASTM D4601, Type II requirements.

>	Siplast Parabase FS

2.02  DESCRIPTION OF SYSTEMS

*   NOTE:	For Item A, choose the base and finish membrane plies in accordance with the project design requirements (ASTM D6163 or ASTM D6164 criteria).

A.	Roofing Membrane Assembly:  A roof membrane assembly consisting of two plies of a prefabricated, reinforced Styrene-Butadiene-Styrene (SBS) block copolymer modified asphalt membrane, applied over a prepared substrate.  Reinforcement mats shall be impregnated/saturated and coated each side with SBS modified bitumen blend.  The assembly shall possess waterproofing capability, such that a phased roof application, with only the modified bitumen base ply in place, can be achieved for prolonged periods of time without detriment to the watertight integrity of the entire roof system.

>	Siplast Paratech hot asphalt/torch-applied roof system

*   NOTE:	For Item 1, choose one of the following base ply options to meet the desired design criteria.

1.	Fiberglass Mat Reinforced Modified Bitumen Base, Stripping and Flashing Reinforcement Ply, manufactured in accordance with ASTM D6163 Type I, Grade S criteria.

>	Paratech Glass Base by Siplast; Dallas, TX

1.	Polyester Mat Reinforced Modified Bitumen Base, Stripping and Flashing Reinforcement Ply, manufactured in accordance with ASTM D6164 Type I, Grade S criteria.

>	Paratech 180 Base by Siplast; Dallas, TX

1.	Polyester Mat Reinforced Modified Bitumen Base, Stripping and Flashing Reinforcement Ply, manufactured in accordance with ASTM D6164 Type II, Grade S criteria.

>	Paratech 250 Base by Siplast; Dallas, TX

*   NOTE:	For Item 2, choose one of the following finish ply options to meet the desired design criteria.

2.	Fiberglass Mat Reinforced Modified Bitumen Finish Ply, manufactured in accordance with ASTM D6163 Type I, Grade G criteria.

>	Paratech Glass Cap FR TG by Siplast; Dallas, TX

2.	Polyester Mat Reinforced Modified Bitumen Finish Ply, manufactured in accordance with ASTM D6164 Type I, Grade G criteria.

>	Paratech 180 Cap FR TG by Siplast; Dallas, TX

2.	Polyester Mat Reinforced Modified Bitumen Finish Ply, manufactured in accordance with ASTM D6164 Type II, Grade G criteria.

>	Paratech 250 Cap FR TG by Siplast; Dallas, TX

B.	Flashing Membrane:  A flashing membrane consisting of a prefabricated, reinforced Styrene-Butadiene-Styrene (SBS) block copolymer modified asphalt membrane, applied over a prepared substrate.  Reinforcement mats shall be impregnated/saturated and coated each side with SBS modified bitumen blend.

*   NOTE:	For Item 1, choose one of the following flashing ply options to meet the desired design criteria.

1.	Torch-applied Polyester Mat Reinforced Modified Bitumen Flashing Ply, manufactured in accordance with ASTM D6164 Type I, Grade G criteria.

>	Paratech 180 Cap FR TG by Siplast; Dallas, TX

1.	Torch-applied Polyester Mat Reinforced Modified Bitumen Flashing Ply, manufactured in accordance with ASTM D6164 Type II, Grade G criteria.

>	Paratech 250 Cap FR TG by Siplast; Dallas, TX

1.	Adhesive-applied Polyester Mat Reinforced Modified Bitumen Flashing Ply, manufactured in accordance with ASTM D6164 Type I, Grade G criteria.

>	Paratech 180 Cap FR by Siplast; Dallas, TX

1.	Adhesive-applied Polyester Mat Reinforced Modified Bitumen Flashing Ply, manufactured in accordance with ASTM D6164 Type II, Grade G criteria.

>	Paratech 250 Cap FR by Siplast; Dallas, TX

C.	Catalyzed Acrylic Resin Flashing System:  A specialty flashing system consisting of a PMMA-based, fully reinforced membrane installed over a prepared or primed substrate.  The flashing system consists of a catalyzed acrylic resin primer, basecoat and topcoat, combined with a non-woven polyester fleece.  The use of the specialty flashing system shall be specifically approved in advance by the membrane manufacturer for each application.

>	Parapro 123 Flashing System by Siplast; Dallas, TX

2.03  ROOFING ACCESSORIES

A.	Roofing Adhesives

1.	Mopping Asphalt:  Type III or IV asphalt certified for full compliance with the requirements listed in Table I, ASTM D312.  Each container or bulk shipping ticket shall indicate the equiviscous temperature, EVT, the finished blowing temperature, FBT, and the flash point, FP.  Mopping asphalt shall be approved in writing by the roof membrane manufacturer.

2.	Flashing Adhesive:  A slump resistant, asphalt cutback flashing adhesive, reinforced with non-asbestos fibers, conforming to ASTM D4586 Type II requirements.

>	Siplast PA-828 Flashing Cement

3.	Mastic:  An asphalt cutback mastic, reinforced with non-asbestos fibers, used as a base for setting metal flanges conforming to ASTM D4586 Type II requirements.

>	Siplast PA-1021 Plastic Cement by Siplast; Dallas, TX

B.	Primers

1.	Primer:  An asphalt/solvent blend meeting ASTM D41, South Coast Air Quality District and Ozone Transport Commission requirements.

>	PA-917 Primer by Siplast; Dallas, TX

2.	Primer:  An asphalt, solvent blend conforming to ASTM D41 requirements.

>	PA-1125 Asphalt Primer by Siplast; Dallas, TX

C.	Sealant (horizontal applications):  A moisture-curing, self-leveling elastomeric sealant designed for roofing applications.  The sealant shall be approved by the roof membrane manufacturer for use in conjunction with the roof membrane materials.  Acceptable types are as follows:

>	PS-209 Elastomeric Sealant by Siplast; Dallas, TX

D.	Sealant (vertical and horizontal applications):  A moisture-curing, non-slump elastomeric sealant designed for roofing applications.  The sealant shall be approved by the roof membrane manufacturer for use in conjunction with the roof membrane materials.  Acceptable types are as follows:

>	PS-715 NS Elastomeric Sealant by Siplast; Dallas, TX

E.	Ceramic Granules:  No. 11 grade specification ceramic granules of color scheme matching the granule surfacing of the finish ply.

F.	Perlite Cant Strips:  A cant strip composed of expanded volcanic minerals combined with waterproofing binders.  The top surface shall be pre-treated with an asphalt based coating.  The face of the cant shall have a nominal 4 inch dimension.

G.	Fasteners

1.	Base Sheet Fasteners:  Base sheet fasteners shall be approved by the manufacturer of the primary roofing products.  Acceptable base sheet fasteners for specific substrate types are listed below.

a)	Lightweight Concrete or Gypsum Substrates

-	A single unit, precision formed, electro zinc coated steel fastener having a 2.7 inch diameter rib reinforced cap and 1.7 inch long rectangular legs, designed to expand when fully driven into the lightweight concrete.  Fasteners for lightweight concrete shall meet FM Standard 4470 requirements for corrosion resistance.

>	Zono-tite Fasteners by Siplast; Dallas, TX

-	A single unit, precision formed, electro zinc coated steel fastener having a 2.7 inch diameter rib reinforced cap and 1 inch long rectangular legs, designed to expand when fully driven into the lightweight concrete.  Fasteners for lightweight concrete shall meet FM Standard 4470 requirements for corrosion resistance.

>	NVS Fasteners by Siplast; Dallas, TX

-	A single unit, precision formed, Galvalume (AZ-55) coated steel fastener having a 2.7 inch cap and a [1.4, 1.8] inch long shank.  The fastener shall incorporate twin high tensile steel wires that facilitate a diverging reverse hook action when driven into the structural substrate.

>	Para-Lok Fastener by Siplast; Dallas, TX

>	OlyLok  Locking Impact Nail by OMG; Agawam, MA

2.	Substrate Panel/Thermal Barrier Fasteners:  Fasteners and plates shall be FM Approved, and/or approved by the manufacturer of the primary roofing products.  Acceptable fastener manufacturers for specific deck types are listed below.

a)	Metal Decks:  Insulation mechanical fasteners for metal decks shall be factory coated for corrosion resistance.  The fastener shall conform meet or exceed Factory Mutual Standard 4470 and when subjected to 30 Kesternich cycles, show less than 15% red rust.  Acceptable insulation fastener types for metal decks are listed below.

-	A fluorocarbon coated screw type roofing fastener having a minimum 0.220 inch thread diameter.  Plates used in conjunction with the fastener shall be a metal type having a minimum 3 inch diameter, as supplied by the fastener manufacturer.

>	Parafast Fastener by Siplast; Dallas, TX

>	Standard RoofGrip Drill Point Fastener by OMG; Agawam, MA

b)	Wood/Plywood Decks:  Insulation mechanical fasteners for wood/plywood decks shall be factory coated for corrosion resistance.  The fastener shall conform meet or exceed Factory Mutual Standard 4470 and when subjected to 30 Kesternich cycles, show less than 15% red rust.  Acceptable insulation fastener types for wood/plywood decks are listed below.

-	A fluorocarbon coated screw type roofing fastener having a minimum 0.220 inch thread diameter.  Plates used in conjunction with the fastener shall be a metal type having a minimum 3 inch diameter, as supplied by the fastener manufacturer.

>	Parafast Fastener by Siplast; Dallas, TX

>	Standard RoofGrip Drill Point Fastener by OMG; Agawam, MA

c)	Structural Concrete Decks:  Insulation mechanical fasteners for structural concrete decks shall be factory coated for corrosion resistance.  The fastener shall conform meet or exceed Factory Mutual Standard 4470 and when subjected to 30 Kesternich cycles, show less than 15% red rust.  Acceptable insulation fastener types for structural concrete decks are listed below.

-	A fluorocarbon coated non-threaded, hammer-driven roofing fastener.  Plates used in conjunction with the fastener shall be a metal type, having a minimum 3 inch diameter, specifically manufactured for use with the structural concrete fastener.

>	Parafast CD-10 Fastener by Siplast; Dallas, TX

>	CD-10 by OMG; Agawam, MA

-	A fluorocarbon coated screw type roofing fastener having a minimum 0.245 inch thread diameter.  Plates used in conjunction with the fastener shall be a metal type having a minimum 3 inch diameter, as supplied by the fastener manufacturer.

>	Parafast HD Fastener by Siplast; Dallas, TX

>	Heavy Duty Roofing Fastener by OMG; Agawam, MA

d)	Cementitious Wood Fiber Decks:  Acceptable insulation fastener types for wood cement fiber decks are listed below.

-	A single unit, precision formed, fluorocarbon coated screw type roofing fastener having a minimum 0.310 inch diameter shank and a minimum 0.710 inch diameter head.  The corresponding plate used shall be a metal type, having a minimum 3 inch diameter, specially manufactured for use with the screw fastener.

>	Parafast LD Fastener with Parafast 3 inch plates by Siplast; Dallas, TX

>	Lite-Deck Fasteners with G-90 3 inch plates by OMG; Agawam, MA

3.	Flashing Reinforcing Sheet Fasteners for Wood/Plywood Substrates to Receive Flashing Coverage:  Fasteners shall be approved by the manufacturer of the primary roofing products.  Acceptable fasteners for specific substrate types are listed below.

a)	Wood/Plywood Substrates

-	A 12 gauge, spiral or annular threaded shank, zinc coated steel roofing fastener having a minimum 1 inch head.

>	Hot-Dip Galvanized Square Cap by Maze Nails; Peru, IL

>	Simplex Cap Nail by Simplex Nails, Inc., Americus, GA

*  NOTE:	Contact Siplast for further information regarding approved base sheet fasteners for specific substrates.

H.	Walktread:  A prefabricated, puncture resistant polyester core reinforced, polymer modified bitumen sheet material topped with a ceramic-coated granule wearing surface.

1.	Thickness: 0.217 in (5.5 mm)

2.	Weight: 1.4 lb/ft² (6.8 kg/m²)

3.	Width: 30 in (76.2 cm)

>	Paratread by Siplast; Dallas, TX

PART 3 EXECUTION

3.01  PREPARATION

*  NOTE:	Edit this section to address specific job conditions which may affect the scope of work.

A.	General:  Sweep or vacuum all surfaces, removing all loose aggregate and foreign substances prior to commencement of roofing.

B.	Asphaltic Primer:  Prime metal and concrete and masonry surfaces with a uniform coating of the specified asphalt primer.

3.02  SUBSTRATE PREPARATION

*  NOTE:	See the Siplast Rigid Insulation and Base Sheet Usage Guide for information regarding approved rigid insulation and applicable installation methods.

*  NOTE:	Select the substrate panel fastening frequency, if applicable, to meet project-specific design criteria.

A.	Substrate Panel/Thermal Barrier:  Install substrate panels with end joints offset; edges of the panels shall be in moderate contact without forcing applied in strict accordance with the insulation manufacturer's requirements and the following instructions.  Install only as much panels as can be made watertight within the same work day.

1.	Mechanically attach the panel to the substrate, using the specified fasteners, at a rate of 1 fastener per [--] square feet of panel area ([----] per 4' x 8' panel).  Increase the fastening frequency by 50% at the perimeter of the roof and mechanically attach the corners at the rate of 1 fastener per 1 square foot of panel area (32 per 4-foot by 8-foot panel).

*  NOTE:	Select the temporary roof application method if one is incorporated into the specified roofing configuration.

B.	Torch Applied Temporary Roof:  Torch apply the ply sheets directly to the prepared substrate, lapping sides and ends a minimum of 3 inches.  Apply the sheets free of wrinkles, creases or fishmouths and exert sufficient pressure on the roll during application to ensure the prevention of air pockets.  Seal each penetration and termination using fiberglass tape and the specified plastic cement to ensure that the temporary roof configuration is completely water-tight.

C.	Hot Asphalt-applied Temporary Roof:  Apply the ply sheets in hot asphalt directly to the concrete/deck substrate, free of wrinkles, creases or fishmouths.  Install each sheet directly behind the asphalt applicator.  Exert sufficient pressure on the roll during application to ensure the prevention of air pockets.

*   NOTE:	Delete the following reference to Specification Section 03 52 00 if existing lightweight insulating concrete or gypsum.

D.	Lightweight Insulating Concrete Roof System:  See Specification Section 03 52 00.

*  NOTE:	Select the base sheet fastening pattern to meet the project design criteria.

E.	Base Sheet Securement to Prepared Substrate:  Lay the base sheet over the entire area to be roofed, lapping sides 3 inches and ends 6 inches.  Using the specified fasteners, fasten each sheet every 7.5 inches through laps and stagger fasten the remainder of the sheet in 2 rows on nominal 12 inch centers with fasteners in each row on 10 inch centers.  Increase the fastening pattern by 70% at the perimeter of the roof and 160% in the corners.

E.	Base Sheet Securement to Prepared Substrate:  Lay the base sheet over the entire area to be roofed, lapping sides 3 inches and ends 6 inches.  Using the specified fasteners, fasten each sheet every 7 inches through laps and stagger fasten the remainder of the sheet in 3 rows on nominal 9 inch centers with fasteners in each row on 10 inch centers.  Increase the fastening pattern by 70% at the perimeter of the roof and 160% in the corners.

3.03  ROOF MEMBRANE INSTALLATION

*  NOTE:	This specification is limited to projects having a maximum roof slope of 1/2 inch.  Contact Siplast for specifications to meet higher slope requirements.

A.	Membrane Application:  Apply roofing in accordance with roofing system manufacturer's instructions and the following requirements.  Application of roofing membrane components shall immediately follow application of insulation as a continuous operation.

B.	Aesthetic Considerations:  Construction of an aesthetically pleasing overall appearance of the finished roof application is a standard requirement for this project.  Make necessary preparations, utilize recommended application techniques, apply the specified materials including granules, and exercise care in ensuring that the finished application is acceptable to the Owner.

C.	Kettles And Tankers:  Kettles and tankers shall be equipped with accurate, fully readable thermometers.  Do not heat asphalt to or above its flash point.  Avoid heating at or above the FBT, should conditions make this impractical, heating must be no more than 25ºF  below the EVT and no more than 25ºF above EVT.

D.	Asphalt Temperatures:  If the EVT information is not provided, the following asphalt temperature shall be observed.  Maximum heating temperature shall be 525ºF (274ºC).  Minimum application temperature shall be 400ºF (204ºC).

E.	Asphalt Moppings:  Ensure that all moppings do not exceed a maximum of 25 lb/sq.  Mopping shall be total in coverage, leaving no breaks or voids.

F.	Bitumen Consistency:  Cutting or alterations of bitumen, primer, and sealants will not be permitted.

G.	Roofing Application:  Apply all layers of roofing free of wrinkles, creases or fishmouths.  Exert sufficient pressure on the roll during application to ensure prevention of air pockets.

*  NOTE:	Use the following items 1-3 for applications incorporating sheets applied perpendicular to the slope of the roof.

1.	Apply all layers of roofing perpendicular to the slope of the deck.

2.	Fully bond the base ply to the prepared substrate, utilizing minimum 3 inch side and end laps.  Apply each sheet directly behind the hot asphalt applicator.  Cut a dog ear angle at the end laps on overlapping selvage edges.  Using a clean trowel, apply top pressure to top seal T-laps immediately following sheet application.  Stagger end laps a minimum of 3 feet.

3.	Fully bond the finish ply to the base ply, utilizing minimum 3 inch side and end laps.  Apply each sheet directly behind the torch applicator.  Stagger end laps of the finish ply a minimum 3 feet.  Cut a dog ear angle at the end laps on overlapping selvage edges.  Using a clean trowel, apply top pressure to top seal T-laps immediately following sheet application.  Stagger side laps of the finish ply a minimum 12 inches from side laps in the underlying base ply.  Stagger end laps of the finish ply a minimum 3 feet from end laps in the underlying base ply.

*  NOTE:	Use the following items 1-3 in for applications incorporating sheets applied parallel to the slope of the roof.

1.	Apply all layers of roofing parallel to the slope of the deck.

2.	Fully bond the base ply to the prepared substrate, utilizing minimum 3 inch side and end laps.  Apply each sheet directly behind the hot asphalt applicator.  Cut dog ear angles on underlying end laps at the finish edge and the overlapping selvage edges.  Using a clean trowel, apply top pressure to top seal T-laps immediately following sheet application.  Stagger end laps a minimum of 3 feet.

3.	Fully bond the finish ply to the base ply, utilizing minimum 3 inch side and end laps.  Apply each sheet directly behind the torch applicator.  Stagger end laps of the finish ply a minimum 3 feet.  Cut dog ear angles on underlying end laps at the finish edge and the overlapping selvage edges.  Using a clean trowel, apply top pressure to top seal T-laps immediately following sheet application.  Stagger side laps of the finish ply a minimum 12 inches from side laps in the underlying base ply.  Stagger end laps of the finish ply a minimum 3 feet from end laps in the underlying base ply.

4.	Maximum sheet lengths and special fastening of the specified roof membrane system may be required at various slope increments where the roof deck slope exceeds 1/2 inch per foot. The manufacturer shall provide acceptable sheet lengths and the required fastening schedule for all roofing sheet applications to applicable roof slopes.

H.	Granule Embedment:  Broadcast mineral granules over all bitumen overruns on the finish ply surface, while the bitumen is still hot or the adhesive is soft, to ensure a monolithic surface color.

I.	Torch-applied Flashing Application - masonry surfaces:  Flash masonry parapet walls and curbs using the reinforcing sheet and the flashing membrane.  After the base ply has been applied to the top of the cant, fully adhere the reinforcing sheet, utilizing minimum 3 inch side laps and extend a minimum of 3 inches onto the base ply surface and up the flashing substrate in accordance with the membrane manufacturer’s requirements.  After the final roofing ply has been applied to the top of the cant, prepare the surface area that is to receive flashing coverage by torch heating granular surfaces or by application of asphalt primer; allowing primer to dry thoroughly. Torch apply the flashing into place using three foot widths (cut off the end of roll) always lapping the factory selvage edge.  Stagger the laps of the flashing layer from lap seams in the reinforcing layer.  Extend the flashing sheet a minimum of 4 inches beyond the toe of the cant onto the prepared surface of the finished roof and up the wall to the desired flashing height.  Exert pressure on the flashing sheet during application to ensure complete contact with the wall/roof surfaces, preventing air pockets.  Check and seal all loose laps and edges.  Nail the top edge of the flashing on 9 inch centers. (See manufacturer's schematic for visual interpretation).

J.	Torch-applied Flashing Application - wood surfaces:  Flash wood or plywood parapet walls and curbs using the reinforcing sheet and the flashing membrane.  The reinforcing sheet shall have minimum 3 inch side laps and extend a minimum of 3 inches onto the base ply surface and up the flashing substrate in accordance with the membrane manufacturer’s requirements.  Nail the reinforcing sheet through the field of the sheet to the vertical wood surface on 12 inch centers from the top of the cant to top of the wall or curb.  Fully adhere the remainder of the flashing reinforcing sheet that extends over the cant and roof level.  After the final roofing ply has been applied to the top of the cant, prepare the surface area that is to receive flashing coverage by torch heating granular surfaces or by application of asphalt primer; allowing primer to dry thoroughly.  Torch apply the flashing into place using three foot widths (cut off the end of roll) always lapping the factory selvage edge.  Extend the flashing sheet a minimum of 4 inches beyond the toe of the cant onto the prepared surface of the finished roof and up the wall to the desired flashing height.  Exert pressure on the flashing sheet during application to ensure complete contact with the wall/roof surfaces, preventing air pockets.  Check and seal all loose laps and edges.  Nail the top edge of the flashing on 9 inch centers. (See manufacturer's schematic for visual interpretation).

K.	Adhesive-applied Flashing Application - Masonry Surfaces:  Flash masonry parapet walls and curbs using the reinforcing sheet and the flashing membrane.  Fully adhere the reinforcing sheet to the substrate.  Incorporate minimum 3 inch laps; extending the sheets a minimum of 3 inches onto the base ply surface and 3 inches up the parapet wall above the cant.  Terminate the finish ply at the top of the cant.  Cut the flashing membrane into lengths that can be easily handled.  Apply a uniform coat of the specified flashing cement to the area to receive flashing coverage.  Set the flashing in place while exerting pressure on the flashing sheet to ensure complete contact with the wall/roof surfaces and to prevent air pockets.  Check and seal all loose laps and edges.  Nail the top edge of the flashing on 9 inch centers.

L.	Adhesive-applied Flashing Application – Wood/Plywood Surfaces: Flash wood/plywood parapet walls and curbs using the reinforcing sheet and the flashing membrane.  Apply the reinforcing sheet to incorporate minimum 3 inch laps, extending the sheets a minimum of 3 inches onto the base ply surface and to the top of the parapet wall, curb, etc.  Nail the reinforcing sheet on 12 inch centers in all directions to the vertical wood surface from the top of the cant to top of wall, curb, etc.  Fully adhere the remainder of sheet that extends over the cant and roof level.  Terminate the finish ply at the top of the cant.  Cut the flashing membrane into lengths that can be easily handled.  Apply a uniform coat of specified flashing cement to the area to receive flashing coverage.  Set the flashing in place while exerting pressure on the flashing sheet to ensure complete contact with the wall/roof surfaces and to prevent air pockets.  Check and seal all loose laps and edges.  Nail the top edge of the flashing on 9 inch centers.

M.	Catalyzed Acrylic Resin Flashing System:  Install the liquid-applied primer and flashing system in accordance with the membrane system manufacturer’s printed installer’s guidelines and other applicable written recommendations as provided by the manufacturer.

N.	Water Cut-Off:  At end of day's work, or when precipitation is imminent, construct a water cut-off at all open edges.  Cut-offs can be built using asphalt or plastic cement and roofing felts, constructed to withstand protracted periods of service.  Cut-offs must be completely removed prior to the resumption of roofing.

O.	Sealant:  Apply a smooth continuous bead of the specified sealant at the exposed finish ply edge transition to metal flashings incorporated into the roof system.

3.04 FIELD QUALITY CONTROL AND INSPECTIONS

A.	Site Condition:  Leave all areas around job site free of debris, roofing materials, equipment and related items after completion of job.

B.	Notification of Completion:  Notify the manufacturer by means of manufacturer's printed Notification of Completion form of job completion in order to schedule a final inspection date.

C.	Final Inspection/Post-Installation Meeting:  Hold a meeting at the completion of the project, attended by all parties that were present at the pre-job conference.  A punch list of items required for completion shall be compiled by the Contractor and the manufacturer's representative.  Complete, sign, and mail the punch list form to the manufacturer's headquarters.

D.	Issuance of the Guarantee:  Complete all post installation procedures and meet the manufacturer's final endorsement for issuance of the specified guarantee.